## Disch. Test
HAWKER POWERSOURCE, INC.
BATTERY DISCHARGE TEST RESULTS
Customer - |  | Superior |  |  |  | Date - |  |  | 1998-07-24
Battery Type - |  | 18-125-13 |  |  |  | Battery # - |  |  | 4A
Serial Number - |  | R60801-1-6 |  |  |  | Time Started - |  |  | 11:40
A.H. Capacity - |  | 750 |  |  |  | Temperature - |  |  | 86
Manufacturer - |  | GBC |  |  |  | Test Rate - |  |  | 125
New - |  | 1994 |  |  |  | No. of Cells - |  |  | 18
|  | Open Circuit | Start Load
Cell No. | Gravity | Voltage-Strt | Voltage | Hr.1 | Hr. 2 | Hr. 3 | Hr. 4 | Hr. 5
1 | 1.275 | 2.08 | 2.01 | 1.92 | 1.84 | 1.76 | 1.66
2 | 1.28 | 2.1 | 2.02 | 1.96 | 1.91 | 1.87 | 1.82
3 | 1.28 | 2.11 | 1.97 | 1.92 | 1.76 | 1.42 | 0
4 | 1.28 | 2.1 | 2.03 | 1.86 | 1.81 | 1.77 | 1.75
5 | 1.28 | 2.09 | 2.04 | 1.88 | 1.83 | 1.79 | 1.77
6 | 1.285 | 2.08 | 2.03 | 1.92 | 1.84 | 1.74 | 1.65
7 | 1.285 | 2.08 | 2.02 | 1.93 | 1.85 | 1.79 | 1.73
8 | 1.285 | 2.11 | 2.05 | 1.96 | 1.89 | 1.83 | 1.79
9 | 1.285 | 2.09 | 2.06 | 1.94 | 1.88 | 1.82 | 1.77
10 | 1.28 | 2.11 | 2.04 | 1.93 | 1.89 | 1.83 | 1.79
11 | 1.28 | 2.09 | 2.03 | 1.95 | 1.88 | 1.79 | 1.74
12 | 1.275 | 2.08 | 2.03 | 1.93 | 1.84 | 1.74 | 1.69
13 | 1.25 | 2.07 | 1.98 | 1.9 | 1.85 | 1.62 | 0
14 | 1.28 | 2.08 | 2.01 | 1.94 | 1.87 | 1.79 | 1.73
15 | 1.29 | 2.15 | 2.02 | 1.93 | 1.86 | 1.79 | 1.75
16 | 1.275 | 2.08 | 1.98 | 1.91 | 1.87 | 1.78 | 1.64
17 | 1.28 | 2.11 | 1.99 | 1.96 | 1.9 | 1.85 | 1.81
18 | 1.28 | 2.09 | 2.01 | 1.93 | 1.8 | 1.74 | 1.63
19
20
21
22
23
24
Time Finished - |  |  | 15:40
Time to reach 1.70 volts/cell - |  |  | 3.6 | Hrs
Unrepaired Capacity (in AH's) - |  |  | 450
Unrepaired Capacity (%) - |  |  | 60%
Estimated Repair Capacity - |  |  | 30%
Repair Cost - |  |  | 1200
Replacement Cost - |  |  | 2600
Repair % of New - |  |  | 46.15%

## Hyd Analysis
HAWKER POWERSOURCE, INC.
HYDROGEN ANALYSIS
PREPARED FOR KELLWOOD - GREENFIELD
Assumptions:
1) Assume all batteries on charge at the same time
2) Hydrogen Lower Explosive Limit (LEL) is 4%
3) Use 1% maximum for hydrogen (H2) concentration
4) Assume 20% overcharge
5) Assume all batteries are 100% discharged
6) Assume all overcharge goes to produce gas - none produces heat
7) Assume all gas is released uniformly during the last 3 hours of charge
8) Hydrogen is 14 times lighter than air - rises quickly and disperses easily
The formula used for this calculation is as follows:
V = (A) X (B) X (C) X (D) = FT3 (cubic feet) of H2 per charge per battery
A = A.H. capacity of battery
B = % overcharge divided by 100
C = .0147708 (FT3 of H2 produced per A.H.)
D = Number of cells in battery
Battery Type # 1
Model - | 18-125-13 |  | Total FT3 of H2/Charge/Battery - | 39.8812
A.H. Capacity - | 750 |  | Total FT3 of H2 for Battery Type # 1 - | 39.8812
Quantity - | 1
# of Cells - | 18
Battery Type # 2
Model - | 18-125F-17 |  | Total FT3 of H2/Charge/Battery - | 53.1749
A.H. Capacity - | 1000 |  | Total FT3 of H2 for Battery Type # 2 - | 106.3498
Quantity - | 2
# of Cells - | 18
Battery Type # 3
Model - | 18-85F-19 |  | Total FT3 of H2/Charge/Battery - | 40.6788
A.H. Capacity - | 765 |  | Total FT3 of H2 for Battery Type # 3 - | 40.6788
Quantity - | 1
# of Cells - | 18
Battery Type # 4
Model - | 12-85F-13 |  | Total FT3 of H2/Charge/Battery - | 18.0795
A.H. Capacity - | 510 |  | Total FT3 of H2 for Battery Type # 4 - | 36.1589
Quantity - | 2
# of Cells - | 12
TOTAL FT3 OF H2 PER CHARGE FOR ALL BATTERIES - |  |  |  |  | 223.0686
TOTAL FT3 OF H2 PER HOUR FOR LAST 3 HOURS OF CHARGE - |  |  |  |  | 74.3562
TOTAL FT3 OF H2 PER MINUTE (CFM) FOR LAST 3 HOURS OF CHARGE - |  |  |  |  | 1.2393
CFM AIR FLOW REQUIRED TO KEEP H2% FROM EXCEEDING 1% - | [5 empty] | 123.927

## Batt Usage
HAWKER POWERSOURCE, INC.
BATTERY USAGE ANALYSIS
PREPARED FOR BAXTER HEALTHCARE
Battery # | 9404 | 8410 | 9202
Model | 24-85-21 | 24-85-21 | 24-85-21
A.H. Capacity | 850 | 850 | 850
A.H. Available (80%) | 680 | 680 | 680
Where used | REC. | SHIP | REC.
Time Start | 16:45 | 16:45 | 16:45
Time Finish | 23:30 | 23:45 | 23:45
Total Time | 6.75 | 7 | 7
Trk hr. start | 4593.8 | 8906 | 5337
Trk hr. finish | 4596.9 | 8908 | 5338
Total trk. time | 3.1 | 2 | 1
Sg. Start | 1.21 | 1.24 | 1.28
Sg. Finish | 1.15 | 1.2 | 1.265
Sg. used | 60 | 40 | 15
Voltage start | 49.3 | 50.2 | 51.2
Voltage Finish | 47.7 | 49.3 | 50.7
A.H. used | 340 | 226.6667 | 85
A.H. used / hr | 50.3704 | 32.381 | 12.1429
A.H. used / trk hr | 109.6774 | 113.3333 | 85
A.H. needed / shift | 402.963 | 259.0476 | 97.1429
# shifts / battery | 1.6875 | 2.625 | 7
# batts / 2 shifts | 1.1852 | 0.7619 | 0.28571
Test Date - 2/13/97

## SPW Payback
SINGLE POINT WATERING PAYBACK ANANLYSIS
PREPARED FOR ABC CUSTOMER
ASSUMPTIONS:
| Number of batteries - |  | 29
| Labor Cost per hour - |  | 22
| Cost of Water System - |  | 7864
| Manual watering time in minutes - |  |  | 18
| SPW watering time in minutes - |  |  | 2
1) ANNUAL BATTERY WATERING COST:
|  |  |  | MANUAL | AQUAMATIC HP
| A) Weekly watering in minutes - |  |  | 522 | 58
| B) Total annual time in minutes - |  |  | 27144 | 3016
| C) Total Annual Time in hours - |  |  | 452.4 | 50.2667
| D) Annual Labor Cost - |  |  | 9952.8 | 1105.8667
| E) First Year Cost - |  |  | 9952.8 | 8969.8667
2) PAYBACK TIME PERIOD:
| A) In months - |  | 10.8149
| B) In years - |  | 0.90124
3) SAVINGS OVER 5 YEAR BATTERY LIFE:
| 1st year - | 982.9333
| 2nd year - | 8846.9333
| 3rd year - | 8846.9333
| 4th year - | 8846.9333
| 5th year - | 8846.9333
| TOTAL - | 36370.6667
Cost savings does not include other factors such as:
1) Ease of watering |  |  | 4) Increased battery life
2) Safety |  |  | 5) Increased battery productivity
3) Accurate filling |  |  | 6) Lower maintenance costs

## KW Batt Comp
HAWKER POWERSOURCE BATTERY COMPARISON
PREPARED FOR ABC COMPANY
|  | ENERGY PLUS | POWERLINE | TOP POWER
| MODEL | 6-E515 | 6-85-11 | 6-85-11
| COST | 839 | 714 | 678
| A.H. Cap. | 515 | 425 | 425
| K.W.H. Cap | 6.06 | 4.92 | 4.92
| LIFE(mos.) | 84 | 84 | 72
| $/A.H. | 1.6291 | 1.68 | 1.5953
| $/K.W.H. | 138.4488 | 145.122 | 137.8049
| $/KWH/Mo. | 1.6482 | 1.7276 | 1.914
| $/KWH/Year | 19.7784 | 20.7317 | 22.9675
| A.H. % Gained | 17.48%
| K.W.H. % Gained | 18.81%
THE POWERLINE BATTERY CARRIES A FIVE YEAR FULL WARRANTY
THE TOP POWER BATTERY CARRIES A FIVE YEAR WARRANTY - THREE FULL AND TWO PRO-RATE
THE ENERGY PLUS BATTERY CARRIES A FIVE YEAR FULL WARRANTY

## Waterless Payback
HAWKER POWERSOURCE "WATER LESS" BATTERY
COST JUSTIFICATION AND PAYBACK ANAYLSIS
PREPARED FOR HAYWOOD COMPANY
ASSUMPTIONS:
| Number of batteries - |  | 1
| Battery Type - |  | 18-125-13
| Cost of Std. Battery - |  | 2700
| Cost of "Water Less" - |  | 3175
| Cost Difference - |  | 475
| Labor Cost per hour - |  | 20
| Manual watering time in minutes - |  |  | 18
"Water Less" Battery needs to be watered four times per year
1) ANNUAL BATTERY WATERING COST:
|  |  |  | MANUAL | WATER LESS
| A) Weekly watering in minutes - |  |  | 18
| B) Total annual time in minutes - |  |  | 936 | 108
| C) Total Annual Time in hours - |  |  | 15.6 | 1.8
| D) Annual Labor Cost - |  |  | 312 | 36
| E) First Year Cost - |  |  | 312 | 511
2) PAYBACK TIME PERIOD:
| A) In months - |  | 19.6538
| B) In years - |  | 1.6378
3) SAVINGS OVER 5 YEAR BATTERY LIFE:
| 1st year - | -199
| 2nd year - | 276
| 3rd year - | 276
| 4th year - | 276
| 5th year - | 276
| 6th year | 312
| TOTAL - | 905

## Energy Plus Comparison
HAWKER POWERSOURCE BATTERY COMPARISON
PREPARED FOR ABC COMPANY
|  | ENERGY PLUS |  | COMPETITOR
| MODEL | 6-E515 |  | 6-93-11
| COST | 809 |  | 750
| A.H. Cap. | 515 |  | 465
| K.W.H. Cap | 6.06 |  | 5.4
| Weight | 498 |  | 456
| Std. Battery Wt. | 438 |  | 456
| LIFE(mos.) | 84 |  | 84
| $/A.H. | 1.5709 |  | 1.6129
| $/K.W.H. | 133.4983 |  | 138.8889
| $/KWH/Mo. | 1.5893 |  | 1.6534
| $/KWH/Year | 19.0712 |  | 19.8413
| A.H. % Gained | 9.709%
| K.W.H. % Gained | 10.89%
| Wt. Diff in Lbs. | 42
| Wt. Diff in % | 8.434%
| Wt. Diff in lbs over std. | 60 |  | 0
| Wt. Diff % over std. | 12.05% |  | 0%
| Price Diff. in $ | #VALUE! | MORE FOR THE ENERGY PLUS
| Price Diff. % | #VALUE! | HIGHER THAN THE COMPETITOR
| A.H. % Gained | #VALUE! | WITH THE ENERGY PLUS
| K.W.H. % Gained | #VALUE! | WITH THE ENERGY PLUS

## Recharge Cost
HAWKER POWERSOURCE, INC.
Recharge cycle energy cost
Prepared for ABC Company
The cost of electrical energy required to recharge a battery
is influenced by many factors:
A) Size of battery ( # of cells and A.H. capacity)
B) Depth of discharge
C) Age of battery
D) Cost of KWH from utility company
K.W.H. capacity of cell - | 1.94
Number of cells - | 12
Percent discharged - | 80%
Cost per K.W.H. - | 0.0345
Charger efficiency - | 84% | (6 cell - 70%, 12-18 cell - 84%, 24 cell - 87% approx.)
Battery efficiency - | 82% | (Typically 80-85%)
Number of batteries - | 7
Cost per recharge cycle - | 0.93282
Cost for fleet per day - | 6.5298
Cost for fleet per year - | 1958.9268